# Temco Controls T3 SNMP Interface Specification

Device: T3 Programmable Controller

MIB Version: 3.4

Date: January 28, 2026

Enterprise OID: 64991 (Temco Controls)

## 1. Overview

This document defines the SNMP (Simple Network Management Protocol) interface for the Temco T3 Controller. The device supports SNMP v1 and v2c for reading and writing I/O points using a standardized Universal Table structure.

## 2. System Information

Base OID: .1.3.6.1.4.1.64991

| OID | Name | Type | Access | Description |
| --- | --- | --- | --- | --- |
| .1.0 | t3MibVersion | STRING | RO | Firmware/MIB revision (e.g., "v3.4"). |

## 3. Universal I/O Tables

All Input and Output points are mapped to universal tables located under the Product ID .1 (.1.3.6.1.4.1.64991.1).

### 3.1 Universal Inputs Table (t3InTable)

OID: .1.3.6.1.4.1.64991.1.1

Access: Read Only

| Suffix | Name | Data Type | Description |
| --- | --- | --- | --- |
| .1 | inputConfigType | INTEGER | Point Configuration: 1=Binary, 2=Analog. |
| .2 | inputAnalogValue | INTEGER | The live analog value (scaled x1000). |
| .3 | inputBinaryValue | INTEGER | The live digital state (0 or 1). |
| .4 | inputDescription | STRING | User-defined label/name for the point. |
| .5 | inputUnits | INTEGER | Engineering Unit ID (See Section 4). |
| .6 | inputRangeMin | INTEGER | Minimum range value. |
| .7 | inputRangeMax | INTEGER | Maximum range value. |

### 3.2 Universal Outputs Table (t3OutTable)

OID: .1.3.6.1.4.1.64991.1.2

Access: Read / Write

| Suffix | Name | Data Type | Description |
| --- | --- | --- | --- |
| .1 | outputConfigType | INTEGER | Point Configuration: 1=Binary, 2=Analog. |
| .2 | outputAnalogValue | INTEGER | Analog value (scaled x1000). Write to control. |
| .3 | outputBinaryValue | INTEGER | Digital state (0 or 1). Write to control. |
| .4 | outputDescription | STRING | User-defined label/name. |
| .5 | outputUnits | INTEGER | Engineering Unit ID (See Section 4). |

## 4. Engineering Units Reference

The T3 Controller reports units using standard BACnet Engineering Unit IDs (ASHRAE 135). The SNMP Agent automatically translates internal ranges to these standard IDs.

### Common Unit IDs (OID Column .5)

| ID | Unit Name | Symbol | Category |
| --- | --- | --- | --- |
| 62 | Degrees Celsius | °C | Temperature |
| 64 | Degrees Fahrenheit | °F | Temperature |
| 56 | Pounds Force per Sq Inch | PSI | Pressure |
| 53 | Pascals | Pa | Pressure |
| 5 | Volts | V | Electrical |
| 3 | Amperes | A | Electrical |
| 84 | Cubic Feet per Minute | CFM | Air Flow |
| 82 | Gallons per Minute | GPM | Liquid Flow |
| 96 | Parts per Million | PPM | Air Quality |
| 98 | Percent | % | Ratio |
| 95 | No Units | - | Digital / Generic |

### Note on Custom Ranges

If a point is configured with a User-Defined Custom Range:

- The agent will report the specific Unit ID if one has been selected in the T3000 software.

- Otherwise, it defaults to ID 95 (No Units) to ensure compatibility.

## 5. Integration Guide

### 5.1 Connection Details

- SNMP Version: v2c

- Community String: public (Read), private (Write) - Default, configurable.

- Port: 161 (UDP)

### 5.2 Example Usage (Net-SNMP)

To walk the entire Input Table:

snmpwalk -v 2c -c public <DEVICE_IP> .1.3.6.1.4.1.64991.1.1

To read the value of Output 1:

snmpget -v 2c -c public <DEVICE_IP> .1.3.6.1.4.1.64991.1.2.2.1

Copyright © 2026 Temco Controls. All rights reserved.