### Instructions

- Review Section 1.6 & 1.7: These new sections define the "Non-Destructive" compatibility strategy.

# Temco_T3_SNMP_v3.4

## 1. T3 Controller MIB Definition (Documentation)

Organization: Temco Controls

Contact: Maurice Duteau (info@temcocontrols.com)

Enterprise ID: 64991

Version: 3.4

Date: January 28, 2026

### 1.1 Revision History

| Version | Date | Notes |
| --- | --- | --- |
| v3.4 | Jan 28, 2026 | Added Legacy Compatibility Strategy & User-Selected Custom Units. |
| v3.3 | Jan 28, 2026 | Official IANA PEN (64991). Added Version OID. |

### 1.2 Enterprise OID Structure

Base OID: .1.3.6.1.4.1.64991

### 1.3 System Information

OID: .1.3.6.1.4.1.64991.1.0

| Suffix | Short Name | Data Type | Description |

| :--- | :--- | :--- | :--- |

| .0 | t3MibVersion | STRING | Returns firmware/MIB revision (e.g., "v3.4"). |

### 1.4 Universal I/O Tables

Rooted under Product ID .1 (.1.3.6.1.4.1.64991.1)

Universal Inputs (t3InTable) -> .1.1

Universal Outputs (t3OutTable) -> .1.2

| Suffix | Short Name | Data Type | Description |
| --- | --- | --- | --- |
| .1 | *ConfigType | INTEGER | 1=Binary, 2=Analog |
| .2 | *AnalogValue | INTEGER | Raw value (x1000) |
| .3 | *BinaryValue | INTEGER | 0 or 1 |
| .4 | *Description | STRING | User Label |
| .5 | *Units | INTEGER | Engineering Unit ID (See Section 1.5) |

### 1.5 Engineering Units Reference (OID .5)

Standard BACnet/ASHRAE 135 IDs used by T3.

| ID | Unit | Category |
| --- | --- | --- |
| 95 | No Units | Digital / Custom |
| 98 | Percent (%) | Ratio |
| 62 | Degrees Celsius (°C) | Temperature |
| 64 | Degrees Fahrenheit (°F) | Temperature |
| 5 | Volts | Electrical |
| 2 | Milliamperes (mA) | Electrical |
| 3 | Amperes | Electrical |
| 56 | PSI | Pressure |
| 53 | Pascals | Pressure |
| 84 | CFM | Flow |
| 82 | GPM | Flow |
| 96 | PPM | Air Quality |
| 73 | Seconds | Time |

### 1.6 Unit Mapping Logic

The SNMP Agent acts as a Translation Layer between Temco's internal legacy ranges and standard SNMP/BACnet codes.

- Standard Ranges (Legacy Safe):

  - The firmware automatically maps internal T3 ranges (e.g., Range 1) to standard BACnet IDs (e.g., ID 62).

  - No database changes are required. Existing sites work immediately upon firmware update.

- Custom Ranges (Future Proof):

  - Default Behavior: If a custom range does not have a specific unit defined, the Agent reports ID 95 (No Units). This prevents errors on legacy sites.

  - Enhanced Behavior: The T3000 software may optionally allow users to tag a Custom Range with a specific BACnet Unit ID. If present, the Agent reports that ID.

### 1.7 Integration Strategy & Roadmap

- Firmware (Immediate): Implement the temco_snmp_bridge.c logic. It supports all standard ranges today and safely defaults custom ranges to "No Units."

- Software (Next Phase): Update T3000 PC Software to add a "BACnet Unit Type" dropdown in the Custom Range dialog. This allows users to assign specific units (like PSI or GPM) to their custom scales.

## 2. Source Code: main/snmp_t3_api.h

Interface Header & Enums

C

#ifndef SNMP_T3_API_H
#define SNMP_T3_API_H

#include <stdint.h>
#include <string.h>

// --- Version Control ---
#define T3_MIB_REVISION "v3.4 (OID: 64991)"

// --- Initialization ---
void t3_snmp_init(void);

// --- BACnet Engineering Units (T3000 / ASHRAE 135 Subset) ---
typedef enum {
    UNITS_NO_UNITS                  = 95,
    UNITS_PERCENT                   = 98,
    UNITS_DEGREES_CELSIUS           = 62,
    UNITS_DEGREES_FAHRENHEIT        = 64,
    UNITS_VOLTS                     = 5,
    UNITS_MILLIAMPERES              = 2,
    UNITS_AMPERES                   = 3,
    UNITS_WATTS                     = 51,
    UNITS_KILOWATTS                 = 48,
    UNITS_KILOWATT_HOURS            = 19,
    UNITS_POUNDS_FORCE_PER_SQ_INCH  = 56, // PSI
    UNITS_PASCALS                   = 53,
    UNITS_KILOPASCALS               = 54,
    UNITS_INCHES_OF_WATER           = 58,
    UNITS_CUBIC_FEET_PER_MINUTE     = 84, // CFM
    UNITS_GALLONS_US_PER_MINUTE     = 82, // GPM
    UNITS_LITERS_PER_SECOND         = 87,
    UNITS_PARTS_PER_MILLION         = 96,
    UNITS_PERCENT_RELATIVE_HUMIDITY = 29,
    UNITS_SECONDS                   = 73,
    UNITS_MINUTES                   = 72,
    UNITS_HOURS                     = 71
} t3_engineering_units_t;

// --- Bridge Functions ---
uint8_t get_input_count(void);
uint8_t get_input_config(uint8_t idx);
int32_t get_input_analog(uint8_t idx);
int32_t get_input_binary(uint8_t idx);
char* get_input_desc(uint8_t idx);
uint8_t get_input_units(uint8_t idx);
int32_t get_input_min(uint8_t idx);
int32_t get_input_max(uint8_t idx);

uint8_t get_output_count(void);
uint8_t get_output_config(uint8_t idx);
int32_t get_output_analog(uint8_t idx);
void    set_output_analog(uint8_t idx, int32_t val);
int32_t get_output_binary(uint8_t idx);
void    set_output_binary(uint8_t idx, int32_t val);
char* get_output_desc(uint8_t idx);
uint8_t get_output_units(uint8_t idx);
int32_t get_output_min(uint8_t idx);
int32_t get_output_max(uint8_t idx);

#endif // SNMP_T3_API_H

## 3. Source Code: main/temco_snmp_bridge.c

Unit Mapper (Safe Translation Layer)

C

#include "snmp_t3_api.h"
#include "user_data.h" 
#include "esp_log.h"

#ifndef MAX_INPUTS
#define MAX_INPUTS 32
#endif
#ifndef MAX_OUTPUTS
#define MAX_OUTPUTS 32
#endif

// --- UNIT MAPPER ---
uint8_t get_input_units(uint8_t idx) 
{
    if (idx >= MAX_INPUTS) return UNITS_NO_UNITS;
    
    // Check if it's a standard T3000 range
    uint8_t range_id = inputs[idx].range;

    switch(range_id) {
        // --- STANDARD RANGES (Safe Legacy Mapping) ---
        case 1: case 6: case 10: return UNITS_DEGREES_CELSIUS;
        case 2: case 7: case 11: return UNITS_DEGREES_FAHRENHEIT;
        case 3: case 40: return UNITS_PERCENT;
        case 44: return UNITS_PERCENT_RELATIVE_HUMIDITY;
        case 8: case 9: return UNITS_VOLTS;
        case 14: case 15: return UNITS_MILLIAMPERES;
        case 16: return UNITS_AMPERES;
        case 55: return UNITS_KILOWATTS;
        case 56: return UNITS_KILOWATT_HOURS;
        case 12: case 50: return UNITS_POUNDS_FORCE_PER_SQ_INCH;
        case 13: return UNITS_PASCALS;
        case 47: return UNITS_KILOPASCALS;
        case 48: return UNITS_INCHES_OF_WATER;
        case 45: return UNITS_CUBIC_FEET_PER_MINUTE;
        case 53: return UNITS_GALLONS_US_PER_MINUTE;
        case 54: return UNITS_LITERS_PER_SECOND;
        case 46: return UNITS_PARTS_PER_MILLION;
        case 51: return UNITS_SECONDS;
        case 52: return UNITS_MINUTES;

        // --- CUSTOM RANGES (Future Proofing) ---
        // Default behavior: Return NO_UNITS (95) for unknown/custom ranges.
        // This ensures legacy sites don't break.
        // Once T3000 supports "Unit Selection", we can fetch that ID here.
        default:
             return UNITS_NO_UNITS;
    }
}

// --- INPUT ACCESSORS ---
uint8_t get_input_count(void) { return MAX_INPUTS; }

uint8_t get_input_config(uint8_t idx) {
    if (idx >= MAX_INPUTS) return 1;
    // Heuristic: If units are NO_UNITS, treat as Binary (1), else Analog (2)
    return (get_input_units(idx) == UNITS_NO_UNITS) ? 1 : 2;
}

int32_t get_input_analog(uint8_t idx) {
    if (idx >= MAX_INPUTS) return 0;
    return inputs[idx].value; 
}

int32_t get_input_binary(uint8_t idx) {
    if (idx >= MAX_INPUTS) return 0;
    return (inputs[idx].value > 0) ? 1 : 0;
}

char* get_input_desc(uint8_t idx) {
    if (idx >= MAX_INPUTS) return "";
    return (char*)inputs[idx].description; 
}

int32_t get_input_min(uint8_t idx) { return 0; } 
int32_t get_input_max(uint8_t idx) { return 0; } 

// --- OUTPUT ACCESSORS ---
uint8_t get_output_count(void) { return MAX_OUTPUTS; }

uint8_t get_output_config(uint8_t idx) {
    if (idx >= MAX_OUTPUTS) return 1;
    return (outputs[idx].range == 0) ? 1 : 2; 
}

int32_t get_output_analog(uint8_t idx) {
    if (idx >= MAX_OUTPUTS) return 0;
    return outputs[idx].value;
}

void set_output_analog(uint8_t idx, int32_t val) {
    if (idx >= MAX_OUTPUTS) return;
    outputs[idx].value = val;
}

int32_t get_output_binary(uint8_t idx) {
    if (idx >= MAX_OUTPUTS) return 0;
    return (outputs[idx].value > 0) ? 1 : 0;
}

void set_output_binary(uint8_t idx, int32_t val) {
    if (idx >= MAX_OUTPUTS) return;
    outputs[idx].value = (val > 0) ? 1000 : 0; 
}

char* get_output_desc(uint8_t idx) {
    if (idx >= MAX_OUTPUTS) return "";
    return (char*)outputs[idx].description;
}

uint8_t get_output_units(uint8_t idx) { return UNITS_NO_UNITS; }
int32_t get_output_min(uint8_t idx) { return 0; }
int32_t get_output_max(uint8_t idx) { return 0; }

## 4. Source Code: main/snmp_t3_tables.c

Native LwIP Agent Implementation

C

#include "esp_log.h"
#include "lwip/apps/snmp.h"
#include "lwip/apps/snmp_table.h"
#include "lwip/apps/snmp_scalar.h"
#include "lwip/apps/snmp_mib2.h"
#include "snmp_t3_api.h"

static const char *TAG = "SNMP_TBL";

// --- VERSION SCALAR ---
static s16_t t3_version_get_value(struct snmp_node_instance* instance, void* value)
{
    const char *ver = T3_MIB_REVISION;
    size_t len = strlen(ver);
    MEMCPY(value, ver, len);
    return (s16_t)len;
}
static const struct snmp_scalar_node t3_version_node = SNMP_SCALAR_CREATE_NODE(
    0, SNMP_NODE_INSTANCE_READ_ONLY, SNMP_ASN1_TYPE_OCTET_STRING, t3_version_get_value, NULL
);

// --- INPUT TABLE ---
static s16_t t3_in_get_value(struct snmp_node_instance* instance, void* value)
{
    u32_t idx = instance->instance_oid.id[0];
    if (idx < 1 || idx > get_input_count()) return SNMP_ERR_NOSUCHINSTANCE;
    uint8_t c_idx = (uint8_t)(idx - 1);

    switch (instance->node->oid) {
        case 1: *(s32_t*)value = get_input_config(c_idx); return sizeof(s32_t);
        case 2: *(s32_t*)value = get_input_analog(c_idx); return sizeof(s32_t);
        case 3: *(s32_t*)value = get_input_binary(c_idx); return sizeof(s32_t);
        case 4: {
            char *d = get_input_desc(c_idx);
            MEMCPY(value, d, strlen(d)); return strlen(d);
        }
        case 5: *(s32_t*)value = get_input_units(c_idx); return sizeof(s32_t);
        case 6: *(s32_t*)value = get_input_min(c_idx); return sizeof(s32_t);
        case 7: *(s32_t*)value = get_input_max(c_idx); return sizeof(s32_t);
        default: return SNMP_ERR_NOSUCHINSTANCE;
    }
}
static const struct snmp_table_col_def t3_in_cols[] = {
    { 1, SNMP_ASN1_TYPE_INTEGER, SNMP_NODE_INSTANCE_READ_ONLY },
    { 2, SNMP_ASN1_TYPE_INTEGER, SNMP_NODE_INSTANCE_READ_ONLY },
    { 3, SNMP_ASN1_TYPE_INTEGER, SNMP_NODE_INSTANCE_READ_ONLY },
    { 4, SNMP_ASN1_TYPE_OCTET_STRING, SNMP_NODE_INSTANCE_READ_ONLY },
    { 5, SNMP_ASN1_TYPE_INTEGER, SNMP_NODE_INSTANCE_READ_ONLY },
    { 6, SNMP_ASN1_TYPE_INTEGER, SNMP_NODE_INSTANCE_READ_ONLY },
    { 7, SNMP_ASN1_TYPE_INTEGER, SNMP_NODE_INSTANCE_READ_ONLY },
};
static const struct snmp_table_node t3_in_table = SNMP_TABLE_CREATE(
    1, t3_in_cols, t3_in_get_value, NULL, NULL, NULL, NULL
);

// --- OUTPUT TABLE ---
static s16_t t3_out_get_value(struct snmp_node_instance* instance, void* value)
{
    u32_t idx = instance->instance_oid.id[0];
    if (idx < 1 || idx > get_output_count()) return SNMP_ERR_NOSUCHINSTANCE;
    uint8_t c_idx = (uint8_t)(idx - 1);

    switch (instance->node->oid) {
        case 1: *(s32_t*)value = get_output_config(c_idx); return sizeof(s32_t);
        case 2: *(s32_t*)value = get_output_analog(c_idx); return sizeof(s32_t);
        case 3: *(s32_t*)value = get_output_binary(c_idx); return sizeof(s32_t);
        case 4: {
            char *d = get_output_desc(c_idx);
            MEMCPY(value, d, strlen(d)); return strlen(d);
        }
        case 5: *(s32_t*)value = get_output_units(c_idx); return sizeof(s32_t);
        default: return SNMP_ERR_NOSUCHINSTANCE;
    }
}
static snmp_err_t t3_out_set_value(struct snmp_node_instance* instance, u16_t len, void* value)
{
    u32_t idx = instance->instance_oid.id[0];
    uint8_t c_idx = (uint8_t)(idx - 1);
    s32_t val = *(s32_t*)value;
    switch (instance->node->oid) {
        case 2: set_output_analog(c_idx, val); return SNMP_ERR_NOERROR;
        case 3: set_output_binary(c_idx, val); return SNMP_ERR_NOERROR;
        default: return SNMP_ERR_NOTWRITABLE;
    }
}
static const struct snmp_table_col_def t3_out_cols[] = {
    { 1, SNMP_ASN1_TYPE_INTEGER, SNMP_NODE_INSTANCE_READ_ONLY },
    { 2, SNMP_ASN1_TYPE_INTEGER, SNMP_NODE_INSTANCE_READ_WRITE },
    { 3, SNMP_ASN1_TYPE_INTEGER, SNMP_NODE_INSTANCE_READ_WRITE },
    { 4, SNMP_ASN1_TYPE_OCTET_STRING, SNMP_NODE_INSTANCE_READ_ONLY },
    { 5, SNMP_ASN1_TYPE_INTEGER, SNMP_NODE_INSTANCE_READ_ONLY },
};
static const struct snmp_table_node t3_out_table = SNMP_TABLE_CREATE(
    2, t3_out_cols, t3_out_get_value, t3_out_set_value, NULL, NULL, NULL
);

// --- REGISTRATION (IANA 64991) ---
static const struct snmp_node* const t3_product_nodes[] = {
    &t3_version_node.node,      // .0
    &t3_in_table.node.node,     // .1
    &t3_out_table.node.node     // .2
};
static const struct snmp_tree_node t3_product_root = SNMP_CREATE_TREE_NODE(
    1, t3_product_nodes
);
static const struct snmp_node* const t3_enterprise_nodes[] = {
    &t3_product_root.node
};
static const struct snmp_tree_node t3_enterprise_root = SNMP_CREATE_TREE_NODE(
    64991, t3_enterprise_nodes
);
static const struct snmp_mib t3_mib = SNMP_MIB_CREATE(
    t3_enterprise_nodes, &t3_enterprise_root.node
);

void t3_snmp_init(void)
{
    ESP_LOGI(TAG, "Initializing T3 SNMP Agent...");
    ESP_LOGI(TAG, "IANA Enterprise ID: 64991 (Temco Controls)");
    snmp_init();
    snmp_set_mibs(&t3_mib, 1);
}

## 5. README (README_SNMP.md)

Markdown

# Temco T3 SNMP Agent Integration (v3.4)

This branch implements the SNMP Agent using **Native ESP-IDF LwIP**. 
**DO NOT use Arduino libraries.**

## 1. Configuration
1. Run `idf.py menuconfig`.
2. Go to **Component config -> LWIP -> SNMP**.
3. Check **Enable SNMP agent**.
4. Save and Exit.

## 2. Implementation Details
* **MIB Definition:** v3.4 (Universal Tables)
* **Enterprise ID:** 64991 (Temco Controls)
* **OID Base:** `.1.3.6.1.4.1.64991.1`
* **Tables:**
  * Inputs: `.1.1.X` (Read Only)
  * Outputs: `.1.2.X` (Read/Write)
* **Engineering Units:** Automatically mapped from T3 `range` settings to BACnet standard IDs.

## 3. How to Compile
1. Ensure the following files are in `main/`:
   * `snmp_t3_api.h`
   * `snmp_t3_tables.c`
   * `temco_snmp_bridge.c`
2. In your `main.c` (or network init file):
   ```c
   #include "snmp_t3_api.h"
   
   // Inside app_main() or after Ethernet/WiFi is connected:
   t3_snmp_init();

## 4. Testing

Use standard SNMP tools (net-snmp) to verify.

Walk the Inputs:

Bash

snmpwalk -v 2c -c public <ESP32_IP> .1.3.6.1.4.1.64991

Verify Output:

You should see the version string v3.4 (OID: 64991) followed by table data.